## Sheet
vessel | machinery | code | name | description | interval | commissioning_date | last_done_date | last_done_running_hours
GL IGUAZU | Emergency Generator | EGE-001 | Lubricating oil level | Check level | Weekly | 23-Jan-14 | 19-Feb-22
GL IGUAZU | Emergency Generator | EGE-002 | Engine Tightness (visual inspection for leaks) | Check tightness and check any leakages | Weekly | 23-Jan-14 | 19-Feb-22
GL IGUAZU | Emergency Generator | EGE-003 | V-belts (check tension and condition) | Check tension and belt condition | Weekly | 23-Jan-14 | 19-Feb-22
GL IGUAZU | Emergency Generator | EGE-004 | Battery and cable connectors | Check battery condition and cable connectors | Weekly | 23-Jan-14 | 19-Feb-22
GL IGUAZU | Emergency Generator | EGE-005 | Operation of Emergency Generator without load | Test without load | Weekly | 23-Jan-14 | 19-Feb-22
GL IGUAZU | Emergency Generator | EGE-006 | Operation of Emergency Generator on load | Test with load | 3 months | 23-Jan-14 | 19-Feb-22
GL IGUAZU | Emergency Generator | EGE-007 | Combustion air Inlet filter | Check filter | 3 months | 23-Jan-14 | 19-Feb-22
GL IGUAZU | Emergency Generator | EGE-008 | Lubricating Oil | Replace oil | 6 months | 23-Jan-14 | 22-Jan-22
GL IGUAZU | Emergency Generator | EGE-009 | Lubricating Oil Filter (every oil changed) | Replace filter | 6 months | 23-Jan-14 | 22-Jan-22
GL IGUAZU | Emergency Generator | EGE-010 | Engine Monitor, warning system maintenance (authorized service personnel) | Check engine monitor | 500 Hours | 23-Jan-14 | 23-Jan-14 | 0
GL IGUAZU | Emergency Generator | EGE-011 | Valve Clearance | Check settings | 500 Hours | 23-Jan-14 | 23-Jan-14 | 0
GL IGUAZU | Emergency Generator | EGE-012 | Cold starting device | Check condition | 1000 Hours | 23-Jan-14 | 23-Jan-14 | 0
GL IGUAZU | Emergency Generator | EGE-013 | V-belts (retension or renew if necessary) | Check tension and renew if necesssary | 1000 Hours | 23-Jan-14 | 18-May-18 | 15.7
GL IGUAZU | Emergency Generator | EGE-014 | Engine mounting (tighten, replace if damaged when necessary) | Check tightness and replace if damaged | 1000 Hours | 23-Jan-14 | 23-Jan-14 | 0
GL IGUAZU | Emergency Generator | EGE-015 | Fastening, hose unions / clips (renew if damaged) | Check condition and renew if damaged | 1000 Hours | 23-Jan-14 | 23-Jan-14 | 0
GL IGUAZU | Emergency Generator | EGE-016 | Fuel filter cartridge | Replace cartridge | 1000 Hours | 23-Jan-14 | 08-Dec-19 | 15.7
GL IGUAZU | Emergency Generator | EGE-017 | Injection valve (to be done by authorized specialist) | Check injection | 1500 Hours | 23-Jan-14 | 23-Jan-14 | 0
GL IGUAZU | Emergency Generator | EGE-018 | V-belts (replacements after 2 years) | Replace V-belts | 24 months | 23-Jan-14 | 24-May-20
GL IGUAZU | Emergency Generator | EGE-019 | F.O Leak Alarm | Test | 3 months | 23-Jan-14 | 04-Dec-21
GL IGUAZU | Emergency Generator | EGE-020 | Cylinder Head High Temp. Alarm | Test | 3 months | 23-Jan-14 | 04-Dec-21
GL IGUAZU | Emergency Generator | EGE-021 | Lub. Oil Low Press. Alarm | Test | 3 months | 23-Jan-14 | 04-Dec-21
GL IGUAZU | Emergency Generator | EGE-022 | Emergency Generator Battery | Replace Batteries | 7 years | 23-Jan-14 | 21-Jun-20