## Sheet
vessel | machinery | code | name | description | interval | commissioning_date | last_done_date | last_done_running_hours
GL IGUAZU | Emergency Fire Pump | EFP-001 | Submerged line bearing | Check up sliding surfaces for points of contact & injury | 8000 Hours | 23-Jan-14 | 06-Jan-19
GL IGUAZU | Emergency Fire Pump | EFP-002 | Mechanical seal | Check up condition of mating surfaces | 8000 Hours | 23-Jan-14 | 06-Jan-19
GL IGUAZU | Emergency Fire Pump | EFP-003 | Mechanical seal | Renew | 20000 Hours | 23-Jan-14 | 06-Jan-19
GL IGUAZU | Emergency Fire Pump | EFP-004 | Shaft | Check up contact points & injury in portions facing packing & bearing. | 8000 Hours | 23-Jan-14 | 06-Jan-19 | 0
GL IGUAZU | Emergency Fire Pump | EFP-005 | Shaft | Check up points of contact, damage & bend in sliding face. | 20000 Hours | 23-Jan-14 | 06-Jan-19 | 0
GL IGUAZU | Emergency Fire Pump | EFP-006 | O-ring | Check up surface damage & condition of deterioration. Renew it if deformed. | 8000 Hours | 23-Jan-14 | 06-Jan-19 | 0
GL IGUAZU | Emergency Fire Pump | EFP-007 | O-ring | Renew | 20000 Hours | 23-Jan-14 | 06-Jan-19 | 0
GL IGUAZU | Emergency Fire Pump | EFP-008 | Impeller | Check up wear & condition of corrosion of all parts, & measure sliding faces in contact with casing rings & a bore of casing rings. | 8000 Hours | 23-Jan-14 | 06-Jan-19 | 0
GL IGUAZU | Emergency Fire Pump | EFP-009 | Casing ring | Check up contact points, wear & condition of corrosion. | 8000 Hours | 23-Jan-14 | 06-Jan-19 | 0
GL IGUAZU | Emergency Fire Pump | EFP-010 | Outer peripheral sections (motor). Vibration | Check with vibrometer, perception | Daily | 23-Jan-14 | 20-Feb-22
GL IGUAZU | Emergency Fire Pump | EFP-011 | Outer peripheral sections (motor). Abnormal noise | Check by sound listening bar, acoustic sense. | Daily | 23-Jan-14 | 20-Feb-22
GL IGUAZU | Emergency Fire Pump | EFP-012 | Outer peripheral sections (motor). Frame termperature | Check by Thermometer perception | Daily | 23-Jan-14 | 20-Feb-22
GL IGUAZU | Emergency Fire Pump | EFP-013 | Outer peripheral sections (motor). Ventilation | Check the inlet & outlet air temperatures as well as flow rate through sense & by using thermometer | Monthly | 23-Jan-14 | 10-Feb-22
GL IGUAZU | Emergency Fire Pump | EFP-014 | Power source. Voltage, current, etc. | Check at instrument panel | Daily | 23-Jan-14 | 20-Feb-22
GL IGUAZU | Emergency Fire Pump | EFP-015 | Periphery of bearing. Bearing sound. | Check with sound listening bar | Daily | 23-Jan-14 | 20-Feb-22
GL IGUAZU | Emergency Fire Pump | EFP-016 | Periphery of bearing. Bearing temperature. | Check with thermometer. | Daily | 23-Jan-14 | 20-Feb-22
GL IGUAZU | Emergency Fire Pump | EFP-017 | Periphery of bearing. Bearing vibration. | Check with vibrometer, perception | Daily | 23-Jan-14 | 20-Feb-22
GL IGUAZU | Emergency Fire Pump | EFP-018 | Periphery of bearing. Discharge grease | Check the color, odor & hardness | 3 months | 23-Jan-14 | 14-Dec-21
GL IGUAZU | Emergency Fire Pump | EFP-019 | Periphery of bearing. Oil leakage |  | Monthly | 23-Jan-14 | 10-Feb-22
GL IGUAZU | Emergency Fire Pump | EFP-020 | Inside of motor. Wiring megOhm | By megger | 3 months | 23-Jan-14 | 14-Dec-21
GL IGUAZU | Emergency Fire Pump | EFP-021 | Odor |  | Daily | 23-Jan-14 | 20-Feb-22
GL IGUAZU | Emergency Fire Pump | EFP-022 | Inside of motor. Dust | Check for free of dust, foreign substance & water | Yearly | 23-Jan-14 | 21-Nov-21
GL IGUAZU | Emergency Fire Pump | EFP-023 | Inside of terminal box. Compressed terminal | Additional tightening of bolts | Yearly | 23-Jan-14 | 21-Nov-21
GL IGUAZU | Emergency Fire Pump | EFP-024 | Inside of terminal box. Terminal stand | Check for dust | Yearly | 23-Jan-14 | 21-Nov-21
GL IGUAZU | Emergency Fire Pump | EFP-025 | Inside of terminal box. Lead wire | Check for scratch & crack on coating | Yearly | 23-Jan-14 | 21-Nov-21
GL IGUAZU | Emergency Fire Pump | EFP-026 | Others. Conditon of coupling section | Check the coupling | Yearly | 23-Jan-14 | 21-Nov-21
GL IGUAZU | Emergency Fire Pump | EFP-027 | Others. Tightening parts. | Check the leg bolts. Etc. | Yearly | 23-Jan-14 | 21-Nov-21