## Sheet
vessel | machinery | code | name | description | interval | commissioning_date | last_done_date | last_done_running_hours
GL IGUAZU | ER Supply Fan No.3 | ERF03-001 | Power supply & operation | Check for voltage, current vibration, noise & fumes | Daily | 23-Jan-14 | 20-Feb-22
GL IGUAZU | ER Supply Fan No.3 | ERF03-002 | Installation & coating | visual check for bolts looness & peeling of paints | 3 months | 23-Jan-14 | 25-Nov-21
GL IGUAZU | ER Supply Fan No.3 | ERF03-003 | Insulation resistance, bet. Winding & ground | Check by megger, result must be higher than the valve specified in 7.1.3 | 3 months | 23-Jan-14 | 25-Nov-21
GL IGUAZU | ER Supply Fan No.3 | ERF03-004 | Terminal box, junction | Visual check, no evidence of water & dust inside the box. | 3 months | 23-Jan-14 | 25-Nov-21
GL IGUAZU | ER Supply Fan No.3 | ERF03-005 | Terminal box, internal check packing. | Visual check, no degradation, damage or deformation. | 3 months | 23-Jan-14 | 25-Nov-21
GL IGUAZU | ER Supply Fan No.3 | ERF03-006 | Impeller | Visual Check for dust, peeling of coating, rust | 2 years | 23-Jan-14 | 16-Apr-21
GL IGUAZU | ER Supply Fan No.3 | ERF03-007 | Motor appearance | Visual Check for dust, peeling of coating, rust | 2 years | 23-Jan-14 | 16-Apr-21
GL IGUAZU | ER Supply Fan No.3 | ERF03-008 | Motor mounting | Visual Check for dust, peeling of coating, rust | 2 years | 23-Jan-14 | 16-Apr-21
GL IGUAZU | ER Supply Fan No.3 | ERF03-009 | Bolts & fasteners packings | Visual check for rust, corrosio degradation, damage & deformation | 2 years | 23-Jan-14 | 16-Apr-21
GL IGUAZU | ER Supply Fan No.3 | ERF03-010 | Motor bearing | Replace | 2 years | 23-Jan-14 | 30-Oct-20