## Sheet
vessel | machinery | code | name | description | interval | commissioning_date | last_done_date | last_done_running_hours
VALIANT SPLENDOR | Auxiliary Boiler | BLR-001 | High Pressure Air Soot Blower | Carry out soot blowing of exhaust gas section during navigation | Daily | 19-May-20 | 22-May-22
VALIANT SPLENDOR | Auxiliary Boiler | BLR-002 | Water Level Gauge | Blow water level gauge | Daily | 19-May-20 | 22-May-22
VALIANT SPLENDOR | Auxiliary Boiler | BLR-003 | Water quality control | Blow boiler water through surface and bottom | Daily | 19-May-20 | 22-May-22
VALIANT SPLENDOR | Auxiliary Boiler | BLR-004 | Water quality control | Analyze boiler water | 3 days | 19-May-20 | 21-May-22
VALIANT SPLENDOR | Auxiliary Boiler | BLR-005 | Feed Water Pump | Check for leaks, abnormal noise, pump gland and pressure gauge | Daily | 19-May-20 | 22-May-22
VALIANT SPLENDOR | Auxiliary Boiler | BLR-006 | Fuel Oil Service Tank | Check level and temperature, drain water | Daily | 19-May-20 | 22-May-22
VALIANT SPLENDOR | Auxiliary Boiler | BLR-007 | Fuel Oil Circulating Pump | Check for leaks, abnormal noise, overheating, vibration and pressure | Daily | 19-May-20 | 22-May-22
VALIANT SPLENDOR | Auxiliary Boiler | BLR-008 | Burner Combustion | Check the status | Daily | 19-May-20 | 22-May-22
VALIANT SPLENDOR | Auxiliary Boiler | BLR-009 | Burner Fuel oil | Check the pressure and heating temperature | Daily | 19-May-20 | 22-May-22
VALIANT SPLENDOR | Auxiliary Boiler | BLR-010 | Exhaust Stack | Check funnel for smoke color | Daily | 19-May-20 | 22-May-22
VALIANT SPLENDOR | Auxiliary Boiler | BLR-011 | Draft fan | Check | Daily | 19-May-20 | 22-May-22
VALIANT SPLENDOR | Auxiliary Boiler | BLR-012 | Burner Assembly | Check for any leakage of piping | Daily | 19-May-20 | 22-May-22
VALIANT SPLENDOR | Auxiliary Boiler | BLR-013 | Burner Assembly Pilot Burner Nozzle | Disassemble and clean | 150 Hours | 19-May-20 | 30-Apr-22 | 6685
VALIANT SPLENDOR | Auxiliary Boiler | BLR-014 | Burner Assembly Low Combustion Nozzle | Disassemble and clean | 150 Hours | 19-May-20 | 30-Apr-22 | 6685
VALIANT SPLENDOR | Auxiliary Boiler | BLR-015 | Burner Assembly High Combustion Nozzle | Disassemble and clean | 150 Hours | 19-May-20 | 30-Apr-22 | 6685
VALIANT SPLENDOR | Auxiliary Boiler | BLR-016 | Burner Assembly Ignition Rod | Clean and check for cracks and adjustment | 150 Hours | 19-May-20 | 30-Apr-22 | 6685
VALIANT SPLENDOR | Auxiliary Boiler | BLR-017 | Burner Assembly Baffle Plate | Disassemble and clean | 150 Hours | 19-May-20 | 30-Apr-22 | 6685
VALIANT SPLENDOR | Auxiliary Boiler | BLR-018 | Burner Assembly Nozzle Pipe | Clean and check for leaks | 150 Hours | 19-May-20 | 30-Apr-22 | 6685
VALIANT SPLENDOR | Auxiliary Boiler | BLR-019 | Wind box | Inspect | 150 Hours | 19-May-20 | 30-Apr-22 | 6685
VALIANT SPLENDOR | Auxiliary Boiler | BLR-020 | Main Burner Y-type Strainer | Clean | Monthly | 19-May-20 | 28-Apr-22
VALIANT SPLENDOR | Auxiliary Boiler | BLR-021 | Pilot Burner Y-type Strainer | Clean | Monthly | 19-May-20 | 28-Apr-22
VALIANT SPLENDOR | Auxiliary Boiler | BLR-022 | Fuel Oil Circulating Pump | Clean fuel oil double strainer | Monthly | 19-May-20 | 28-Apr-22
VALIANT SPLENDOR | Auxiliary Boiler | BLR-023 | Fuel Oil Circulating Pump | Clean pump built in filter | Monthly | 19-May-20 | 28-Apr-22
VALIANT SPLENDOR | Auxiliary Boiler | BLR-024 | Flame Eye | Inspect and clean protection glass | Monthly | 19-May-20 | 28-Apr-22
VALIANT SPLENDOR | Auxiliary Boiler | BLR-025 | Safety System Function Test | Ignation failure alarm | Monthly | 19-May-20 | 28-Apr-22
VALIANT SPLENDOR | Auxiliary Boiler | BLR-026 | Safety System Function Test | Fan abnormal stop alarm | Monthly | 19-May-20 | 28-Apr-22
VALIANT SPLENDOR | Auxiliary Boiler | BLR-027 | Safety System Function Test | Flame-out alarm | Monthly | 19-May-20 | 28-Apr-22
VALIANT SPLENDOR | Auxiliary Boiler | BLR-028 | Safety System Function Test | Low oil pressure alarm | Monthly | 19-May-20 | 28-Apr-22
VALIANT SPLENDOR | Auxiliary Boiler | BLR-029 | Safety System Function Test | Low and high oil temperature alarm | Monthly | 19-May-20 | 28-Apr-22
VALIANT SPLENDOR | Auxiliary Boiler | BLR-030 | Safety System Function Test | Exhaust gas high temperature alarm | Monthly | 19-May-20 | 28-Apr-22
VALIANT SPLENDOR | Auxiliary Boiler | BLR-031 | Safety System Function Test | Low water level alarm | Monthly | 19-May-20 | 28-Apr-22
VALIANT SPLENDOR | Auxiliary Boiler | BLR-032 | Safety System Function Test | Low low water level alarm | Monthly | 19-May-20 | 28-Apr-22
VALIANT SPLENDOR | Auxiliary Boiler | BLR-033 | Cascade tank filter | Cleaning | 2 Months | 19-May-20 | 19-Apr-22
VALIANT SPLENDOR | Auxiliary Boiler | BLR-034 | Pilot Burner Fuel Pump | Clean T-type auto-cleaner | 3 Months | 19-May-20 | 23-Mar-22
VALIANT SPLENDOR | Auxiliary Boiler | BLR-035 | Fuel Oil Circulating Pump | Clean T-type auto-cleaner | 3 Months | 19-May-20 | 25-Mar-22
VALIANT SPLENDOR | Auxiliary Boiler | BLR-036 | Fuel Oil Circulating Pump | Inspection and adjustment of discharge pressure | 3 Months | 19-May-20 | 25-Mar-22
VALIANT SPLENDOR | Auxiliary Boiler | BLR-037 | Fuel Pressure Regulating Valve | Inspection and adjustment | 3 Months | 19-May-20 | 25-Mar-22
VALIANT SPLENDOR | Auxiliary Boiler | BLR-038 | Fuel Oil Solenoid Valves | Inspection and cleaning | 3 Months | 19-May-20 | 25-Mar-22
VALIANT SPLENDOR | Auxiliary Boiler | BLR-039 | Draft Fan | Inspection of fan | 3 Months | 19-May-20 | 25-Mar-22
VALIANT SPLENDOR | Auxiliary Boiler | BLR-040 | Draft Fan | Inspection and adjustment of drive part of dampers (combustion opening control damper and fully open - fully close damper) | 3 Months | 19-May-20 | 25-Mar-22
VALIANT SPLENDOR | Auxiliary Boiler | BLR-041 | Draft Fan Electric Motor | Measurement of insulation resistance | 3 Months | 19-May-20 | 25-Mar-22
VALIANT SPLENDOR | Auxiliary Boiler | BLR-042 | Fuel Oil Circulating Pump Electric Motor | Measurement of insulation resistance | 3 Months | 19-May-20 | 25-Mar-22
VALIANT SPLENDOR | Auxiliary Boiler | BLR-043 | Pilot Burner Fuel Pump Electric Motor | Measurement of insulation resistance | 3 Months | 19-May-20 | 25-Mar-22
VALIANT SPLENDOR | Auxiliary Boiler | BLR-044 | Fuel Oil Heater | Measurement of insulation resistance | 3 Months | 19-May-20 | 25-Mar-22
VALIANT SPLENDOR | Auxiliary Boiler | BLR-045 | Fuel Oil Heater | Cleaning and inspection | 6 months | 19-May-20 | 21-Apr-22
VALIANT SPLENDOR | Auxiliary Boiler | BLR-046 | Atmospheric Condenser | Clean SW side and check sacrificial anodes | 6 months | 19-May-20 | 25-Nov-21
VALIANT SPLENDOR | Auxiliary Boiler | BLR-047 | Safety Valve | Operation test | 6 months | 19-May-20 | 21-Apr-22
VALIANT SPLENDOR | Auxiliary Boiler | BLR-048 | Water Tubes on ME Exhaust Gas Side | Clean by air blow and collect soots | 3 Months | 19-May-20 | 19-Mar-22
VALIANT SPLENDOR | Auxiliary Boiler | BLR-049 | Water Tubes on GE No.1 Exhaust Gas Side | Clean by air blow and collect soots | 3 Months | 19-May-20 | 25-Mar-22
VALIANT SPLENDOR | Auxiliary Boiler | BLR-050 | Water Tubes on GE No.2 Exhaust Gas Side | Clean by air blow and collect soots | 3 Months | 19-May-20 | 19-Mar-22
VALIANT SPLENDOR | Auxiliary Boiler | BLR-051 | Water Tubes on GE No.3 Exhaust Gas Side | Clean by air blow and collect soots | 3 Months | 19-May-20 | 19-Mar-22
VALIANT SPLENDOR | Auxiliary Boiler | BLR-052 | Boiler Combustion Chamber and Furnace | Inspection and clean by air blow | 6 months | 19-May-20 | 24-Feb-22
VALIANT SPLENDOR | Auxiliary Boiler | BLR-053 | Electric Parts in the Control Panel (Relay, Sequencer, Sequencer Battery) | Noise, vibration, overhaeat, looseness of terminal | 6 months | 19-May-20 | 21-Apr-22
VALIANT SPLENDOR | Auxiliary Boiler | BLR-054 | Fuel Oil Thermostat | Inspection and adjustment (RT type) | 6 months | 19-May-20 | 21-Apr-22
VALIANT SPLENDOR | Auxiliary Boiler | BLR-055 | Steam Pressure Switch | Inspection and adjustment (RT type) | 6 months | 19-May-20 | 21-Apr-22
VALIANT SPLENDOR | Auxiliary Boiler | BLR-056 | Fuel Oil Pressure Switches | Inspection and adjustment (RT type) | 6 months | 19-May-20 | 21-Apr-22
VALIANT SPLENDOR | Auxiliary Boiler | BLR-057 | Fuel Oil Flexible Tubes | Inspection | 1 Year | 19-May-20 | 22-Feb-22
VALIANT SPLENDOR | Auxiliary Boiler | BLR-058 | Fuel Oil Flexible Tubes | Inspection of quick connect coupling o-ring | 1 Year | 19-May-20 | 22-Feb-22
VALIANT SPLENDOR | Auxiliary Boiler | BLR-059 | Flame Detector | Voltage check | 1 Year | 19-May-20 | 22-Feb-22
VALIANT SPLENDOR | Auxiliary Boiler | BLR-060 | Fuel Oil Circulating Pump | Inspection and adjustment of coupling Check deformation of rubber | 1 Year | 19-May-20 | 22-Feb-22
VALIANT SPLENDOR | Auxiliary Boiler | BLR-061 | Fuel Oil Circulating Pump | Overhauling | 2 Years | 19-May-20 | 19-May-22
VALIANT SPLENDOR | Auxiliary Boiler | BLR-062 | Fuel Oil Circulating Pump Electric Motor | Overhauling | 2 Years | 19-May-20 | 19-May-22
VALIANT SPLENDOR | Auxiliary Boiler | BLR-063 | Boiler Combustion Chamber and Furnace | Clean and collect soots through wind box | When Docked | 19-May-20 | 19-May-20
VALIANT SPLENDOR | Auxiliary Boiler | BLR-064 | Feed Water Check Valve | Inspection and recondition | When Docked | 19-May-20 | 19-May-20
VALIANT SPLENDOR | Auxiliary Boiler | BLR-065 | Inside Chimney | Carry out inspection | When Docked | 19-May-20 | 19-May-20
VALIANT SPLENDOR | Auxiliary Boiler | BLR-066 | Valves on Boiler | Recondition and inspection | When Docked | 19-May-20 | 19-May-20
VALIANT SPLENDOR | Auxiliary Boiler | BLR-067 | Cascade Tank | Cleaning | When Docked | 19-May-20 | 19-May-20
VALIANT SPLENDOR | Auxiliary Boiler | BLR-068 | Differencial Pressure Transmitter | Inspection of inside and adjustment | When Docked | 19-May-20 | 19-May-20